## CKV413C3J2G
CHECK VALVE DATA SHEET
TAG. No. |  | CKV413C3J2G
SIZE : |  | 2, 12 | in
PIPING CLASS : |  | CS1SC2 | [9 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | FIRE WATER
M E C H A N I C A L
VALVE TYPE : |  | SWING CHECK VALVE | [13 empty] | RATING / CLASS: | 125
END CONNECTIONS: |  | FLANGED |  | X |  |  |  |  | FACING: |  | FF |  |  |  | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [13 empty] | OTHER
ENDS SIZE & PRESSURE CLASS PER: | [6 empty] | ASME B16.5 | [5 empty] | ASME B16.11 |  |  |  |  | OTHER |  | ASME B16.1
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  |  | API 6D | [5 empty] | API 608 |  |  | API 602 |  |  |  |  | OTHER |  | MSS SP-136
APPLICABLE STANDARDS/SPECIFICATIONS :
DESIGN PRESSURE : |  | 200 |  |  |  |  | PSIG @100°F | [6 empty] | DESIGN TEMP: |  | -20 |  | F. MIN |  | 100 |  | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [7 empty] | PSIG |  |  |  | TEST PRESSURE:
CONTAMINANTS : |  | CO2: | [7 empty] | CHLORIDE: | [5 empty] | H2S:
|  | METHANOL : | [9 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM A536 GRADE 65-45-12 | [11 empty] | TRIM: |  |  | BY MNF
BONNET GASKET: |  | NON METALLIC FLAT GASKET EPDM | [11 empty] | PACKING: |  |  | BY MNF
SEAT: |  | BRONZE | [11 empty] | SEALS: |  |  | BY MNF
SYSTEM: |  | SWING CHECK VALVE
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | UL LISTED / FM APPROVED, PIN: AISI 304, DISC: IRON EPDM ENCAPSULATED, BOLTED COVER, INSTALLATION: HORIZONTAL OR VERTICAL
N O T E S
1. | Piping Class Doc. No.MTU-ES-01 V1

## GAV413C3J2G
GATE VALVE DATA SHEET
TAG. No. |  | GAV413C3J2G
SIZE : |  | 2, 3, 4, 6, 8, 10, 12, 12 | in
PIPING CLASS : |  | CS1SC2 | [9 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | FIRE WATER
M E C H A N I C A L
VALVE TYPE : |  | GATE VALVE | [13 empty] | RATING / CLASS: | 125
END CONNECTIONS: |  | FLANGED |  | X |  |  |  |  | FACING: |  | FF |  |  |  | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [13 empty] | OTHER
ENDS SIZE & PRESSURE CLASS PER: | [6 empty] | ASME B16.5 | [5 empty] | ASME B16.11 |  |  |  |  | OTHER |  | ASME B16.1
TYPE OPERATOR : |  | HANDWHEEL OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  |  | API 6D | [5 empty] | API 608 |  |  | API 602 |  |  |  |  | OTHER |  | MSS SP-128 TYPE II
APPLICABLE STANDARDS/SPECIFICATIONS :
DESIGN PRESSURE : |  | 200 |  |  |  |  | PSIG @100°F | [6 empty] | DESIGN TEMP: |  | -20 |  | F. MIN |  | 100 |  | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [7 empty] | PSIG |  |  |  | TEST PRESSURE:
CONTAMINANTS : |  | CO2: | [7 empty] | CHLORIDE: | [5 empty] | H2S:
|  | METHANOL : | [9 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM A536 GRADE 65-45-12 | [11 empty] | PACKING: |  |  | EPDM
BONNET GASKET: |  | NON METALLIC FLAT GASKET EPDM
SEALS: |  | BY MNF
STEM : |  | BRONZE
SEAT: |  | BY MNF
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | UL LISTED / FM APPROVED, SOLID WEDGE, WEDGE: DUCTILE IRON EPDM ENCAPSULATED, STEM: OS&Y/RSNRO, BONNET BOLTING AS PER MANUFACTURER'S STD WITH SURFACE PROTECTION
N O T E S
1. | Piping Class Doc. No.MTU-ES-01 V1

## GAV41H4J2G
GATE VALVE DATA SHEET
TAG. No. |  | GAV41H4J2G
SIZE : |  | 1/2, 1 | in
PIPING CLASS : |  | CS1SC2 | [8 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | FIRE WATER
M E C H A N I C A L
VALVE TYPE : |  | GATE VALVE | [12 empty] | RATING / CLASS: | 150
END CONNECTIONS: |  | FLANGED | [5 empty] | FACING: | [5 empty] | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [12 empty] | OTHER |  | NPTF
ENDS SIZE & PRESSURE CLASS PER: | [5 empty] | ASME B16.5 | [5 empty] | ASME B16.11 |  |  |  |  | OTHER |  | ASME B1.20.1
TYPE OPERATOR : |  | HANDWHEEL OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  | API 6D | [5 empty] | API 608 |  |  | API 602 |  |  |  |  | OTHER |  | MSS SP-80
APPLICABLE STANDARDS/SPECIFICATIONS :
DESIGN PRESSURE : |  | 200 |  |  |  | PSIG @100°F | [6 empty] | DESIGN TEMP: |  | -20 |  | F. MIN |  | 100 |  | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [6 empty] | PSIG |  |  |  | TEST PRESSURE:
CONTAMINANTS : |  | CO2: | [6 empty] | CHLORIDE: | [5 empty] | H2S:
|  | METHANOL : | [8 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM B62 UNS C83600 | [10 empty] | PACKING: |  |  | LUBRICATED FIBER / GRAPHITE
BONNET GASKET: |  | -
SEALS: |  | BY MNF
STEM : |  | BRONZE
SEAT: |  | RINGS: BRONZE
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | SOLID WEDGE, STEM: OS&Y/RSNRO, INTEGRAL SEATS, DISC: BRONZE, SCREWED BONNET
N O T E S
1. | Piping Class Doc. No.MTU-ES-01 V1

## GLV415J4J2G
GLOBE VALVE DATA SHEET
TAG. No. |  | GLV415J4J2G
SIZE : |  | 2-1/2 | in
PIPING CLASS : |  | CS1SC2 | [8 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | FIRE WATER
M E C H A N I C A L
VALVE TYPE : |  | ANGLE HOSE VALVE | [12 empty] | RATING / CLASS: | 300 PSI CWP
END CONNECTIONS: |  | FLANGED | [5 empty] | FACING: | [5 empty] | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [12 empty] | OTHER |  | NPTFxNH
ENDS SIZE & PRESSURE CLASS PER: | [5 empty] | ASME B16.5 | [5 empty] | ASME B16.11 |  |  |  |  | OTHER |  | ASME B1.20.1 / NFPA 1963
TYPE OPERATOR : |  | HANDWHEEL OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  | API 6D | [5 empty] | API 608 |  |  | API 602 |  |  |  |  | OTHER |  | MSS SP-80
APPLICABLE STANDARDS/SPECIFICATIONS :
DESIGN PRESSURE : |  | 200 |  |  |  | PSIG @100°F | [6 empty] | DESIGN TEMP: |  | -20 |  | F. MIN |  | 100 |  | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [6 empty] | PSIG |  |  |  | TEST PRESSURE:
CONTAMINANTS : |  | CO2: | [6 empty] | CHLORIDE: | [5 empty] | H2S:
|  | METHANOL : | [8 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM B62 UNS C83600 | [10 empty] | TRIM:
BONNET GASKET: |  | - | [10 empty] | PACKING: |  |  | NON ASBESTOS ARAMID FIBERS WITH GRAPHITE
YOKE BEARINGS: |  | BY MNF | [10 empty] | SEALS: |  |  | BY MNF
STEM : |  | BRONZE
SEAT: |  | DISC: RUBBER
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | UL LISTED / FM APPROVED, OUTLET WITH CAP AND CHAIN, RISING STEM, RENEWABLE DISC, INTEGRAL SEAT, DISC: BRONZE, SCREWED-IN BONNET
N O T E S
1. | Piping Class Doc: MTU-ES-01 V1

## GLV41H4J2G
GLOBE VALVE DATA SHEET
TAG. No. |  | GLV41H4J2G
SIZE : |  | 3/4, 1-1/2, 2 | in
PIPING CLASS : |  | CS1SC2 | [8 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | FIRE WATER
M E C H A N I C A L
VALVE TYPE : |  | GLOBE VALVE | [12 empty] | RATING / CLASS: | 150
END CONNECTIONS: |  | FLANGED | [5 empty] | FACING: | [5 empty] | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [12 empty] | OTHER |  | NPTF
ENDS SIZE & PRESSURE CLASS PER: | [5 empty] | ASME B16.5 | [5 empty] | ASME B16.11 |  |  |  |  | OTHER |  | ASME B1.20.1
TYPE OPERATOR : |  | HANDWHEEL OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  | API 6D | [5 empty] | API 608 |  |  | API 602 |  |  |  |  | OTHER |  | MSS SP-80
APPLICABLE STANDARDS/SPECIFICATIONS :
DESIGN PRESSURE : |  | 200 |  |  |  | PSIG @100°F | [6 empty] | DESIGN TEMP: |  | -20 |  | F. MIN |  | 100 |  | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [6 empty] | PSIG |  |  |  | TEST PRESSURE:
CONTAMINANTS : |  | CO2: | [6 empty] | CHLORIDE: | [5 empty] | H2S:
|  | METHANOL : | [8 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM B62 UNS C83600 | [10 empty] | TRIM:
BONNET GASKET: |  | - | [10 empty] | PACKING: |  |  | LUBRICATED FIBER / GRAPHITE
YOKE BEARINGS: |  | BY MNF | [10 empty] | SEALS: |  |  | BY MNF
STEM : |  | BRONZE
SEAT: |  | RINGS: BRONZE
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | SWIVEL PLUG DISC, DISC: BRONZE, SCREWED BONNET, STEM: IS/RSRO, UL LISTED
N O T E S
1. | Piping Class Doc: MTU-ES-01 V1