## Sheet1
ITEM | Catalogacion | LINE_NUM | SPEC | TYPE | TYPE_CODE | DESCRIPTION | FIRST_SIZE_NUMBER | SECOND_SIZE_NUMBER | SCH | FACE | RATING | QTY | UNITS | WEIGHT_PER_UNIT | TOTAL_WEIGHT | NOTE
1 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 12,00 | - | 20 | BE | - | 5 | m | 49,71 | 248,55 | -
2 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 12,00 | - | 20 | BW | - | 1 | e.a | 46,06 | 46,06 | -
3 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x20 | 12,00 | 8 | 20x20 | BW | - | 1 | e.a | 10,16 | 10,16 | -
4 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDx20 | 14,00 | 12 | STDx20 | BW | - | 1 | e.a | 31,1 | 31,1 | -
5 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 1 | e.a | 17,3 | 17,3 | -
6 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
7 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
8 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
9 | - | CS1SC2-12"-SCI-1-7-150 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
10 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 12,00 | - | 20 | BE | - | 5 | m | 49,71 | 248,55 | -
11 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 12,00 | - | 20 | BW | - | 1 | e.a | 46,06 | 46,06 | -
12 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x20 | 12,00 | 8 | 20x20 | BW | - | 1 | e.a | 10,16 | 10,16 | -
13 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDx20 | 14,00 | 12 | STDx20 | BW | - | 1 | e.a | 31,1 | 31,1 | -
14 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 1 | e.a | 17,3 | 17,3 | -
15 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
16 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
17 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
18 | - | CS1SC2-12"-SCI-1-7-151 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
19 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 12,00 | - | 20 | BE | - | 4 | m | 49,71 | 198,84 | -
20 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 12,00 | - | 20 | BW | - | 1 | e.a | 46,06 | 46,06 | -
21 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x20 | 12,00 | 8 | 20x20 | BW | - | 1 | e.a | 10,16 | 10,16 | -
22 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDx20 | 14,00 | 12 | STDx20 | BW | - | 1 | e.a | 31,1 | 31,1 | -
23 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 1 | e.a | 17,3 | 17,3 | -
24 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
25 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
26 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
27 | - | CS1SC2-12"-SCI-1-7-152 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
28 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 12,00 | - | 20 | BE | - | 4 | m | 49,71 | 198,84 | -
29 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 12,00 | - | 20 | BW | - | 1 | e.a | 46,06 | 46,06 | -
30 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x20 | 12,00 | 8 | 20x20 | BW | - | 1 | e.a | 10,16 | 10,16 | -
31 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDx20 | 14,00 | 12 | STDx20 | BW | - | 1 | e.a | 31,1 | 31,1 | -
32 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 1 | e.a | 17,3 | 17,3 | -
33 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
34 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
35 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
36 | - | CS1SC2-12"-SCI-1-7-153 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
37 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 1 | m | 81,33 | 81,33 | -
38 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 34,00 | 34,00 | -
39 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
40 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 1 | e.a | 0,23 | 0,23 | -
41 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
42 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 12 | e.a | 0,873 | 10,476 | -
43 | - | CS1SC2-14"-SCI-1-7-133 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 12 | e.a | 0,957 | 11,484 | -
44 | - | CS1SC2-14"-SCI-1-7-134 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 55 | m | 81,33 | 4473,15 | -
45 | - | CS1SC2-14"-SCI-1-7-134 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 4 | e.a | 68,00 | 272,00 | -
46 | - | CS1SC2-14"-SCI-1-7-134 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
47 | - | CS1SC2-14"-SCI-1-7-135 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 1 | m | 81,33 | 81,33 | -
48 | - | CS1SC2-14"-SCI-1-7-135 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 2 | e.a | 68,00 | 136,00 | -
49 | - | CS1SC2-14"-SCI-1-7-135 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
50 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 1 | m | 81,33 | 81,33 | -
51 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 34,00 | 34,00 | -
52 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
53 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 1 | e.a | 0,23 | 0,23 | -
54 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
55 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 12 | e.a | 0,873 | 10,476 | -
56 | - | CS1SC2-14"-SCI-1-7-138 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 12 | e.a | 0,957 | 11,484 | -
57 | - | CS1SC2-14"-SCI-1-7-139 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 49 | m | 81,33 | 3985,17 | -
58 | - | CS1SC2-14"-SCI-1-7-139 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 4 | e.a | 68,00 | 272,00 | -
59 | - | CS1SC2-14"-SCI-1-7-139 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
60 | - | CS1SC2-14"-SCI-1-7-140 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 3 | m | 81,33 | 243,99 | -
61 | - | CS1SC2-14"-SCI-1-7-140 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 68,00 | 68,00 | -
62 | - | CS1SC2-14"-SCI-1-7-140 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
63 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 1 | m | 81,33 | 81,33 | -
64 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 34,00 | 34,00 | -
65 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
66 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 1 | e.a | 0,23 | 0,23 | -
67 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
68 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 12 | e.a | 0,873 | 10,476 | -
69 | - | CS1SC2-14"-SCI-1-7-143 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 12 | e.a | 0,957 | 11,484 | -
70 | - | CS1SC2-14"-SCI-1-7-144 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 43 | m | 81,33 | 3497,19 | -
71 | - | CS1SC2-14"-SCI-1-7-144 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 4 | e.a | 68,00 | 272,00 | -
72 | - | CS1SC2-14"-SCI-1-7-144 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
73 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 3 | m | 81,33 | 243,99 | -
74 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 68,00 | 68,00 | -
75 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 1 | e.a | 50,49 | 50,49 | -
76 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 1 | e.a | 0,23 | 0,23 | -
77 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
78 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 12 | e.a | 0,873 | 10,476 | -
79 | - | CS1SC2-14"-SCI-1-7-145 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 12 | e.a | 0,957 | 11,484 | -
80 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 63 | m | 81,33 | 5123,79 | -
81 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 4 | e.a | 68,00 | 272,00 | -
82 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | FT | NIP | NIPPLE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BExTE, SCH 160 L= 100 mm | 2,5 | 100mm | 160 | BExTE | - | 16 | e.a | 1,49 | 23,84 | -
83 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 3 | e.a | 93,00 | 279,00 | -
84 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 30 | 14,00 | 2,5 | STDx30 | BW | - | 17 | e.a | 0,00 | 0,00 | -
85 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 4 | e.a | 50,49 | 201,96 | -
86 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | VL | GLB | ANGLE HOSE VALVE THD, MSS SP-80, B62 UNS C83600, 300 PSI CWP, FNPTxNH W/CAP AND CHAIN, FNPT B1.20.1 AND NH NFPA 1963, SCREW-IN BONNET, RENEWABLE DISC, PKG NON ASBESTOS, DISC&STEM BRONZE, RISING STEM, HO, UL LISTED/FM APPROVED | 2,5 | - | - | FNPTxMNH | 300 PSI CWP | 16 | e.a | 7,08 | 113,28 | -
87 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 3 | e.a | 0,23 | 0,69 | -
88 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 36 | e.a | 0,00 | 0,00 | -
89 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 36 | e.a | 0,873 | 31,428 | -
90 | - | CS1SC2-14"-SCI-1-7-146 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 36 | e.a | 0,957 | 34,452 | -
91 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 124 | m | 81,33 | 10084,92 | -
92 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 5 | e.a | 34,00 | 170,00 | -
93 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 10 | e.a | 68,00 | 680,00 | -
94 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDxSTD | 16,00 | 14 | STDxSTD | BW | - | 2 | e.a | 43,8 | 87,6 | -
95 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 2 | e.a | 93,00 | 186,00 | -
96 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 16,00 | - | STD | BW | - | 1 | e.a | 115,00 | 115,00 | -
97 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 14,00 | - | STD | FF | 150 | 12 | e.a | 50,49 | 605,88 | -
98 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 14,00 | - | - | FF | 125 | 6 | e.a | 284,00 | 1704,00 | -
99 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 14,00 | - | - | FF | 150 | 12 | e.a | 0,23 | 2,76 | -
100 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 144 | e.a | 0,00 | 0,00 | -
101 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 145mm | - | - | - | 144 | e.a | 0,873 | 125,712 | -
102 | - | CS1SC2-14"-SCI-1-7-148 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 170mm | - | - | - | 144 | e.a | 0,957 | 137,808 | -
103 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 14,00 | - | STD | BE | - | 1 | m | 81,33 | 81,33 | -
104 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 16,00 | - | STD | BE | - | 40 | m | 93,27 | 3730,8 | -
105 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 14,00 | - | STD | BW | - | 1 | e.a | 68,00 | 68,00 | -
106 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 16,00 | - | STD | BW | - | 1 | e.a | 89,2 | 89,2 | -
107 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDxSTD | 16,00 | 14 | STDxSTD | BW | - | 1 | e.a | 43,8 | 43,8 | -
108 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDxSTD | 16,00 | 14 | STDxSTD | BW | - | 1 | e.a | 43,8 | 43,8 | -
109 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 16,00 | - | STD | BW | - | 3 | e.a | 115,00 | 345,00 | -
110 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 16,00 | - | STD | FF | 150 | 5 | e.a | 61,68 | 308,4 | -
111 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 16,00 | - | - | FF | 125 | 1 | e.a | 370,00 | 370,00 | -
112 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 16,00 | - | - | FF | 150 | 3 | e.a | 0,3 | 0,9 | -
113 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 48 | e.a | 0,00 | 0,00 | -
114 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 150mm | - | - | - | 48 | e.a | 0,89 | 42,72 | -
115 | - | CS1SC2-16"-SCI-1-7-130 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 180mm | - | - | - | 48 | e.a | 0,991 | 47,568 | -
116 | - | CS1SC2-16"-SCI-1-7-131 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 16,00 | - | STD | BE | - | 2 | m | 93,27 | 186,54 | -
117 | - | CS1SC2-16"-SCI-1-7-131 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 16,00 | - | STD | FF | 150 | 1 | e.a | 61,68 | 61,68 | -
118 | - | CS1SC2-16"-SCI-1-7-136 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 16,00 | - | STD | BE | - | 2 | m | 93,27 | 186,54 | -
119 | - | CS1SC2-16"-SCI-1-7-136 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 16,00 | - | STD | FF | 150 | 1 | e.a | 61,68 | 61,68 | -
120 | - | CS1SC2-16"-SCI-1-7-141 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 16,00 | - | STD | BE | - | 2 | m | 93,27 | 186,54 | -
121 | - | CS1SC2-16"-SCI-1-7-141 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 16,00 | - | STD | FF | 150 | 1 | e.a | 61,68 | 61,68 | -
122 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH STD | 16,00 | - | STD | BE | - | 180 | m | 93,27 | 16788,6 | -
123 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 16,00 | - | STD | BW | - | 5 | e.a | 48,00 | 240,00 | -
124 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STD | 16,00 | - | STD | BW | - | 6 | e.a | 89,2 | 535,2 | -
125 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH STDxSTD | 16,00 | 14 | STDxSTD | BW | - | 3 | e.a | 43,8 | 131,4 | -
126 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH STD | 16,00 | - | STD | FF | 150 | 8 | e.a | 61,68 | 493,44 | -
127 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 16,00 | - | - | FF | 125 | 3 | e.a | 370,00 | 1110,00 | -
128 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 16,00 | - | - | FF | 150 | 5 | e.a | 0,3 | 1,5 | -
129 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 0mm | - | - | - | 80 | e.a | 0,00 | 0,00 | -
130 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 150mm | - | - | - | 80 | e.a | 0,89 | 71,2 | -
131 | - | CS1SC2-16"-SCI-1-7-147 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 1,00 | 180mm | - | - | - | 80 | e.a | 0,991 | 79,28 | -
132 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 30 | 2,5 | - | 30 | BE | - | 10 | m | 8,04 | 80,4 | -
133 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | FT | ERE | ECCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40x30 | 6,00 | 2,5 | 40x30 | BW | - | 3 | e.a | 0,00 | 0,00 | -
134 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | FT | NIP | NIPPLE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BExTE, SCH 160 L= 100 mm | 2,5 | 100mm | 160 | BExTE | - | 10 | e.a | 1,49 | 14,9 | -
135 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 2,5 | - | 30 | BW | - | 7 | e.a | 2,69 | 18,83 | -
136 | 3028812.0 | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 3 | e.a | 10,91 | 32,73 | -
137 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | VL | GAT | HOSE GATE VALVE THD, MSS SP-80, B62 UNS C83600, 300 PSI CWP, FNPTxNH W/CAP AND CHAIN, FNPT B1.20.1 AND NH NFPA 1963, SCREWED BONNET, PKG NON ASBESTOS, SOLID WEDGE, WEDGE B62, SEAT&STEM BRONZE, NON RISING STEM, HO, UL LISTED/FM APPROVED | 2,5 | - | - | FNPTxMNH | 300 PSI CWP | 3 | e.a | 8,39 | 25,17 | -
138 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | VL | GLB | ANGLE HOSE VALVE THD, MSS SP-80, B62 UNS C83600, 300 PSI CWP, FNPTxNH W/CAP AND CHAIN, FNPT B1.20.1 AND NH NFPA 1963, SCREW-IN BONNET, RENEWABLE DISC, PKG NON ASBESTOS, DISC&STEM BRONZE, RISING STEM, HO, UL LISTED/FM APPROVED | 2,5 | - | - | FNPTxMNH | 300 PSI CWP | 4 | e.a | 7,08 | 28,32 | -
139 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 6,00 | - | - | FF | 150 | 3 | e.a | 0,06 | 0,18 | -
140 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 24 | e.a | 0,00 | 0,00 | -
141 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 115mm | - | - | - | 24 | e.a | 0,401 | 9,624 | -
142 | - | CS1SC2-2 1/2"-SCI-1-7-162 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 125mm | - | - | - | 24 | e.a | 0,42 | 10,08 | -
143 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 30 | 4,00 | - | 30 | BE | - | 155 | m | 12,91 | 2001,05 | -
144 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 4,00 | - | 30 | BW | - | 2 | e.a | 1,95 | 3,9 | -
145 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 4,00 | - | 30 | BW | - | 7 | e.a | 3,9 | 27,3 | -
146 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | FT | CRE | CONCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40x30 | 6,00 | 4 | 40x30 | BW | - | 1 | e.a | 3,9 | 3,9 | -
147 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 4,00 | - | 30 | FF | 150 | 2 | e.a | 7,11 | 14,22 | -
148 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 2,00 | - | - | FF | 125 | 1 | e.a | 19,00 | 19,00 | -
149 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 2,00 | - | - | FF | 150 | 1 | e.a | 0,03 | 0,03 | -
150 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 1 | e.a | 0,05 | 0,05 | -
151 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
152 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 12 | e.a | 0,235 | 2,82 | -
153 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 8 | e.a | 0,254 | 2,032 | -
154 | - | CS1SC2-4"-SCI-1-7-159 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 90mm | - | - | - | 4 | e.a | 0,222 | 0,888 | -
155 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 30 | 4,00 | - | 30 | BE | - | 2 | m | 12,91 | 25,82 | -
156 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x30 | 8,00 | 4 | 20x30 | BW | - | 1 | e.a | 28,00 | 28,00 | -
157 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 4,00 | - | 30 | FF | 150 | 1 | e.a | 7,11 | 7,11 | -
158 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 1 | e.a | 0,05 | 0,05 | -
159 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
160 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 8 | e.a | 0,235 | 1,88 | -
161 | - | CS1SC2-4"-SCI-1-7-160 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 8 | e.a | 0,254 | 2,032 | -
162 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 30 | 4,00 | - | 30 | BE | - | 2 | m | 12,91 | 25,82 | -
163 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x30 | 8,00 | 4 | 20x30 | BW | - | 1 | e.a | 28,00 | 28,00 | -
164 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 4,00 | - | 30 | FF | 150 | 1 | e.a | 7,11 | 7,11 | -
165 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 1 | e.a | 0,05 | 0,05 | -
166 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
167 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 8 | e.a | 0,235 | 1,88 | -
168 | - | CS1SC2-4"-SCI-1-7-161 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 8 | e.a | 0,254 | 2,032 | -
169 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 30 | 4,00 | - | 30 | BE | - | 2 | m | 12,91 | 25,82 | -
170 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x30 | 8,00 | 4 | 20x30 | BW | - | 1 | e.a | 28,00 | 28,00 | -
171 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 4,00 | - | 30 | FF | 150 | 1 | e.a | 7,11 | 7,11 | -
172 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 1 | e.a | 0,05 | 0,05 | -
173 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
174 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 8 | e.a | 0,235 | 1,88 | -
175 | - | CS1SC2-4"-SCI-1-7-165 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 8 | e.a | 0,254 | 2,032 | -
176 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 45 | m | 28,26 | 1271,7 | -
177 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 4 | e.a | 10,2 | 40,8 | -
178 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | FT | NIP | NIPPLE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BExTE, SCH 160 L= 100 mm | 2,5 | 100mm | 160 | BExTE | - | 4 | e.a | 1,49 | 5,96 | -
179 | 3028337.0 | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 1 | e.a | 16,48 | 16,48 | -
180 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 30 | 6,00 | 2,5 | 40x30 | BW | - | 4 | e.a | 1,81 | 7,24 | -
181 | 3028812.0 | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 2 | e.a | 10,91 | 21,82 | -
182 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | VL | GLB | ANGLE HOSE VALVE THD, MSS SP-80, B62 UNS C83600, 300 PSI CWP, FNPTxNH W/CAP AND CHAIN, FNPT B1.20.1 AND NH NFPA 1963, SCREW-IN BONNET, RENEWABLE DISC, PKG NON ASBESTOS, DISC&STEM BRONZE, RISING STEM, HO, UL LISTED/FM APPROVED | 2,5 | - | - | FNPTxMNH | 300 PSI CWP | 4 | e.a | 7,08 | 28,32 | -
183 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 6,00 | - | - | FF | 150 | 2 | e.a | 0,06 | 0,12 | -
184 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
185 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 115mm | - | - | - | 16 | e.a | 0,401 | 6,416 | -
186 | - | CS1SC2-6"-SCI-1-7-149 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 125mm | - | - | - | 16 | e.a | 0,42 | 6,72 | -
187 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 1 | m | 28,26 | 28,26 | -
188 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x40 | 8,00 | 6 | 20x40 | BW | - | 1 | e.a | 28,00 | 28,00 | -
189 | 3028812.0 | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 1 | e.a | 10,91 | 10,91 | -
190 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 2 | e.a | 17,3 | 34,6 | -
191 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 6,00 | - | - | FF | 150 | 1 | e.a | 0,06 | 0,06 | -
192 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
193 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
194 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 115mm | - | - | - | 8 | e.a | 0,401 | 3,208 | -
195 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
196 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 125mm | - | - | - | 8 | e.a | 0,42 | 3,36 | -
197 | - | CS1SC2-6"-SCI-1-7-157 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
198 | - | CS1SC2-6"-SCI-1-7-158 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 151 | m | 28,26 | 4267,26 | -
199 | - | CS1SC2-6"-SCI-1-7-158 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 2 | e.a | 5,1 | 10,2 | -
200 | - | CS1SC2-6"-SCI-1-7-158 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 8 | e.a | 10,2 | 81,6 | -
201 | 3028812.0 | CS1SC2-6"-SCI-1-7-158 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 1 | e.a | 10,91 | 10,91 | -
202 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 259 | m | 28,26 | 7319,34 | -
203 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 1 | e.a | 5,1 | 5,1 | -
204 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 9 | e.a | 10,2 | 91,8 | -
205 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40x30 | 6,00 | 3 | 40x30 | BW | - | 2 | e.a | 16,00 | 32,00 | -
206 | 3028337.0 | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 4 | e.a | 16,48 | 65,92 | -
207 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 3,00 | - | 30 | FF | 150 | 2 | e.a | 4,97 | 9,94 | -
208 | 3028812.0 | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 6 | e.a | 10,91 | 65,46 | -
209 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 3,00 | - | - | FF | 125 | 2 | e.a | 29,00 | 58,00 | -
210 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 3,00 | - | - | FF | 150 | 4 | e.a | 0,03 | 0,12 | -
211 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 2 | e.a | 0,05 | 0,1 | -
212 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 6,00 | - | - | FF | 150 | 8 | e.a | 0,06 | 0,48 | -
213 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 32 | e.a | 0,00 | 0,00 | -
214 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 32 | e.a | 0,235 | 7,52 | -
215 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 110mm | - | - | - | 16 | e.a | 0,248 | 3,968 | -
216 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 16 | e.a | 0,254 | 4,064 | -
217 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 64 | e.a | 0,00 | 0,00 | -
218 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 115mm | - | - | - | 64 | e.a | 0,401 | 25,664 | -
219 | - | CS1SC2-6"-SCI-1-7-163 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 125mm | - | - | - | 64 | e.a | 0,42 | 26,88 | -
220 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 156 | m | 28,26 | 4408,56 | -
221 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 10 | e.a | 10,2 | 102,00 | -
222 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40x30 | 6,00 | 3 | 40x30 | BW | - | 2 | e.a | 16,00 | 32,00 | -
223 | 3028337.0 | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 4 | e.a | 16,48 | 65,92 | -
224 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 30 | 3,00 | - | 30 | FF | 150 | 2 | e.a | 4,97 | 9,94 | -
225 | 3028812.0 | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 40 | 6,00 | - | 40 | FF | 150 | 6 | e.a | 10,91 | 65,46 | -
226 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | VL | GAT | GATE VALVE FL, MSS SP-128 TYPE II, A536 Gr 65-45-12, CL 125, FF, B16.1, BB, NON METALLIC FLAT GASKET EPDM, PKG EPDM, SOLID WEDGE, WEDGE DUCTILE IRON EPDM ENCAPSULATED, STEM BRONZE, OS&Y/RSNRO, HO, UL LISTED/FM APPROVED | 3,00 | - | - | FF | 125 | 2 | e.a | 29,00 | 58,00 | -
227 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 3,00 | - | - | FF | 150 | 4 | e.a | 0,03 | 0,12 | -
228 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 4,00 | - | - | FF | 150 | 2 | e.a | 0,05 | 0,1 | -
229 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 6,00 | - | - | FF | 150 | 8 | e.a | 0,06 | 0,48 | -
230 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 0mm | - | - | - | 32 | e.a | 0,00 | 0,00 | -
231 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 100mm | - | - | - | 32 | e.a | 0,235 | 7,52 | -
232 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 110mm | - | - | - | 16 | e.a | 0,248 | 3,968 | -
233 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,625 | 115mm | - | - | - | 16 | e.a | 0,254 | 4,064 | -
234 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 64 | e.a | 0,00 | 0,00 | -
235 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 115mm | - | - | - | 64 | e.a | 0,401 | 25,664 | -
236 | - | CS1SC2-6"-SCI-1-7-164 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 125mm | - | - | - | 64 | e.a | 0,42 | 26,88 | -
237 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | PP | PE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, PE, SCH 80 | 1,00 | - | 80 | PE | - | 7 | m | 3,24 | 22,68 | -
238 | 3028590.0 | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FT | 90L | ELBOW 90 DEG, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 1,00 | - | - | SW | 3000 | 2 | e.a | 0,35 | 0,7 | -
239 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FT | CPL | COUPLING, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 1,00 | - | - | SW | 3000 | 2 | e.a | 0,22 | 0,44 | -
240 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FT | NIP | NIPPLE, SMLS, CS, ASTM A106 GR B, ASME B36.10, PE, SCH 80 L= 100 mm | 0,75 | 100mm | 80 | PE | - | 2 | e.a | 0,22 | 0,44 | -
241 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FT | NIP | NIPPLE, SMLS, CS, ASTM A106 GR B, ASME B36.10, PE, SCH 80 L= 100 mm | 1,00 | 100mm | 80 | PE | - | 2 | e.a | 0,324 | 0,648 | -
242 | 3028601.0 | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FT | RTE | REDUCING TEE, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 1,00 | 0,75 | - | SW | 3000 | 1 | e.a | 0,53 | 0,53 | -
243 | 3028718.0 | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | FL | SW | SOCKETWELD FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,9 | 2,7 | -
244 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | VL | BAL | BALL VALVE W/INTEGRAL WELDED 2 NIPPLES, FB, FLOATING BALL, API 608, API 598, A105, CL 800, SW W/2 PE NIPPLES, MNF STD, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, API 607, LO | 0,75 | - | - | PE | 800 | 1 | e.a | 2,4 | 2,4 | -
245 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,035 | 0,105 | -
246 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 0mm | - | - | - | 4 | e.a | 0,00 | 0,00 | -
247 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 70mm | - | - | - | 4 | e.a | 0,125 | 0,5 | -
248 | - | CS2SA1-1"-ALV-1-5-018 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 75mm | - | - | - | 4 | e.a | 0,129 | 0,516 | -
249 | - | CS2SA1-10"-PRO-1-6-015 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 10,00 | - | 30 | BE | - | 4 | m | 51,01 | 204,04 | -
250 | - | CS2SA1-10"-PRO-1-6-015 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 10,00 | - | 30 | BW | - | 1 | e.a | 36,77 | 36,77 | -
251 | - | CS2SA1-10"-PRO-1-6-015 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 10,00 | - | 30 | RF | 150 | 15 | e.a | 23,57 | 353,55 | -
252 | - | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 10,00 | - | 30 | BE | - | 4 | m | 51,01 | 204,04 | -
253 | - | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 10,00 | - | 30 | BW | - | 1 | e.a | 36,77 | 36,77 | -
254 | - | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 10,00 | - | 30 | RF | 150 | 15 | e.a | 23,57 | 353,55 | -
255 | - | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 10,00 | - | - | RF | 150 | 3 | e.a | 266,00 | 798,00 | -
256 | - | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 10,00 | - | - | RF | 150 | 3 | e.a | 0,598 | 1,794 | -
257 | 3029342.0 | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
258 | 3029342.0 | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 125mm | - | - | - | 12 | e.a | 0,592 | 7,104 | -
259 | 3029342.0 | CS2SA1-10"-PRO-1-6-016 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 145mm | - | - | - | 12 | e.a | 0,643 | 7,716 | -
260 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 24,00 | - | 30 | BE | - | 5 | m | 209,65 | 1048,25 | -
261 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 24,00 | - | 30 | BW | - | 1 | e.a | 443,55 | 443,55 | -
262 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 30 | 24,00 | 10 | 30x30 | BW | - | 1 | e.a | 17,69 | 17,69 | -
263 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 10,00 | - | 30 | RF | 150 | 3 | e.a | 23,57 | 70,71 | -
264 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 24,00 | - | 30 | RF | 150 | 15 | e.a | 129,5 | 1942,5 | -
265 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 24,00 | - | - | RF | 150 | 3 | e.a | 1580,00 | 4740,00 | -
266 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 10,00 | - | - | RF | 150 | 3 | e.a | 0,598 | 1,794 | -
267 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 24,00 | - | - | RF | 150 | 3 | e.a | 2,216 | 6,648 | -
268 | 3029342.0 | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
269 | 3029342.0 | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 125mm | - | - | - | 12 | e.a | 0,592 | 7,104 | -
270 | 3029342.0 | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 145mm | - | - | - | 12 | e.a | 0,643 | 7,716 | -
271 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,25 | 190mm | - | - | - | 20 | e.a | 1,721 | 34,42 | -
272 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 0mm | - | - | - | 20 | e.a | 0,00 | 0,00 | -
273 | - | CS2SA1-24"-PRO-1-6-011 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 220mm | - | - | - | 20 | e.a | 2,36 | 47,2 | -
274 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 24,00 | - | 30 | BE | - | 6 | m | 209,65 | 1257,9 | -
275 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 24,00 | - | 30 | BW | - | 1 | e.a | 443,55 | 443,55 | -
276 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 30 | 24,00 | 10 | 30x30 | BW | - | 1 | e.a | 17,69 | 17,69 | -
277 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 10,00 | - | 30 | RF | 150 | 3 | e.a | 23,57 | 70,71 | -
278 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 24,00 | - | 30 | RF | 150 | 15 | e.a | 129,5 | 1942,5 | -
279 | - | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 10,00 | - | - | RF | 150 | 3 | e.a | 0,598 | 1,794 | -
280 | 3029342.0 | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
281 | 3029342.0 | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 125mm | - | - | - | 12 | e.a | 0,592 | 7,104 | -
282 | 3029342.0 | CS2SA1-24"-PRO-1-6-012 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 145mm | - | - | - | 12 | e.a | 0,643 | 7,716 | -
283 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | PP | PE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, PE, SCH 80 | 1,00 | - | 80 | PE | - | 1 | m | 3,24 | 3,24 | -
284 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 2,00 | - | 40 | BE | - | 1 | m | 5,44 | 5,44 | -
285 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 10,00 | - | 30 | BE | - | 1 | m | 51,01 | 51,01 | -
286 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 24,00 | - | 30 | BE | - | 375 | m | 209,65 | 78618,75 | -
287 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 24,00 | - | 30 | BW | - | 6 | e.a | 159,35 | 956,1 | -
288 | 3028591.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | 90L | ELBOW 90 DEG, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 0,75 | - | - | SW | 3000 | 1 | e.a | 0,24 | 0,24 | -
289 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 10,00 | - | 30 | BW | - | 2 | e.a | 31,3 | 62,6 | -
290 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 24,00 | - | 30 | BW | - | 11 | e.a | 318,7 | 3505,7 | -
291 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | CPL | COUPLING, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 0,75 | - | - | SW | 3000 | 1 | e.a | 0,14 | 0,14 | -
292 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | CPL | COUPLING, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 1,00 | - | - | SW | 3000 | 2 | e.a | 0,22 | 0,44 | -
293 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | NIP | NIPPLE, SMLS, CS, ASTM A106 GR B, ASME B36.10, PE, SCH 80 L= 100 mm | 0,75 | 100mm | 80 | PE | - | 6 | e.a | 0,22 | 1,32 | -
294 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | SOL | SOCKOLET, CS, ASTM A105, MSS SP-97, SW, CLASS 3000 | 24,00 | 0,75 | - | SW | 3000 | 1 | e.a | 0,15 | 0,15 | -
295 | 3028322.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | TEE | STRAIGHT TEE, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 0,75 | - | - | SW | 3000 | 1 | e.a | 0,33 | 0,33 | -
296 | 3028321.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | TEE | STRAIGHT TEE, CS, ASTM A105, ASME B16.11, SW, CLASS 3000 | 1,00 | - | - | SW | 3000 | 1 | e.a | 0,53 | 0,53 | -
297 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 24,00 | - | 30 | BW | - | 2 | e.a | 443,55 | 887,1 | -
298 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 30 | 24,00 | 10 | 30x30 | BW | - | 2 | e.a | 17,69 | 35,38 | -
299 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 40 | 24,00 | 2 | 30x40 | BW | - | 2 | e.a | 0,79 | 1,58 | -
300 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 40 | 24,00 | 4 | 30x40 | BW | - | 1 | e.a | 2,86 | 2,86 | -
301 | 3028718.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FL | SW | SOCKETWELD FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,9 | 2,7 | -
302 | 3028631.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 2,00 | - | 40 | RF | 150 | 6 | e.a | 2,55 | 15,3 | -
303 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 10,00 | - | 30 | RF | 150 | 6 | e.a | 23,57 | 141,42 | -
304 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 24,00 | - | 30 | RF | 150 | 12 | e.a | 129,5 | 1554,00 | -
305 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | VL | BAL | BALL VALVE W/INTEGRAL WELDED 2 NIPPLES, FB, FLOATING BALL, API 608, API 598, A105, CL 800, SW W/2 PE NIPPLES, MNF STD, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, API 607, LO | 0,75 | - | - | PE | 800 | 2 | e.a | 2,4 | 4,8 | -
306 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | VL | BAL | BALL VALVE FL, FB, LP, FLOATING BALL, API 608, A216 GR WCB, CL 150, RF, B16.5, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, SPW SS304/GRAPH, API 607, LO | 2,00 | - | - | RF | 150 | 6 | e.a | 15,00 | 90,00 | -
307 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 10,00 | - | - | RF | 150 | 3 | e.a | 266,00 | 798,00 | -
308 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 24,00 | - | - | RF | 150 | 3 | e.a | 1580,00 | 4740,00 | -
309 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,035 | 0,105 | -
310 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 2,00 | - | - | RF | 150 | 12 | e.a | 0,097 | 1,164 | -
311 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 10,00 | - | - | RF | 150 | 9 | e.a | 0,598 | 5,382 | -
312 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 24,00 | - | - | RF | 150 | 12 | e.a | 2,216 | 26,592 | -
313 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 0mm | - | - | - | 4 | e.a | 0,00 | 0,00 | -
314 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 70mm | - | - | - | 4 | e.a | 0,125 | 0,5 | -
315 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 75mm | - | - | - | 4 | e.a | 0,129 | 0,516 | -
316 | 3029340.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
317 | 3029340.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 100mm | - | - | - | 16 | e.a | 0,235 | 3,76 | -
318 | 3029340.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 90mm | - | - | - | 16 | e.a | 0,222 | 3,552 | -
319 | 3029342.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 0mm | - | - | - | 36 | e.a | 0,00 | 0,00 | -
320 | 3029342.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 125mm | - | - | - | 36 | e.a | 0,592 | 21,312 | -
321 | 3029342.0 | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,875 | 145mm | - | - | - | 36 | e.a | 0,643 | 23,148 | -
322 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,25 | 190mm | - | - | - | 80 | e.a | 1,721 | 137,68 | -
323 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 0mm | - | - | - | 80 | e.a | 0,00 | 0,00 | -
324 | - | CS2SA1-24"-PRO-1-6-013 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 220mm | - | - | - | 80 | e.a | 2,36 | 188,8 | -
325 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 3,00 | - | 40 | BE | - | 1 | m | 11,29 | 11,29 | -
326 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 3,00 | - | 40 | BW | - | 1 | e.a | 2,03 | 2,03 | -
327 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 40 | 24,00 | 3 | 30x40 | BW | - | 1 | e.a | 1,81 | 1,81 | -
328 | 3028632.0 | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 3,00 | - | 40 | RF | 150 | 6 | e.a | 4,97 | 29,82 | -
329 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, HO | 3,00 | - | - | RF | 150 | 3 | e.a | 34,00 | 102,00 | -
330 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 3,00 | - | - | RF | 150 | 6 | e.a | 0,148 | 0,888 | -
331 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
332 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 100mm | - | - | - | 8 | e.a | 0,235 | 1,88 | -
333 | - | CS2SA1-3"-SUM-1-6-021 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 110mm | - | - | - | 8 | e.a | 0,248 | 1,984 | -
334 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 4,00 | - | 40 | BE | - | 6 | m | 16,08 | 96,48 | -
335 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 4,00 | - | 40 | BW | - | 3 | e.a | 3,9 | 11,7 | -
336 | 3028338.0 | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 4,00 | - | 40 | BW | - | 1 | e.a | 8,44 | 8,44 | -
337 | 3028633.0 | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 4,00 | - | 40 | RF | 150 | 9 | e.a | 7,11 | 63,99 | -
338 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | VL | BAL | BALL VALVE FL, FB, LP, FLOATING BALL, API 608, A216 GR WCB, CL 150, RF, B16.5, A105 + ENP BALL, SS410 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, SPW SS304/GRAPH, API 607, LO | 4,00 | - | - | RF | 150 | 3 | e.a | 45,00 | 135,00 | -
339 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 4,00 | - | - | RF | 150 | 6 | e.a | 0,235 | 1,41 | -
340 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
341 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 100mm | - | - | - | 16 | e.a | 0,235 | 3,76 | -
342 | - | CS2SA1-4"-PRO-1-6-017 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 115mm | - | - | - | 16 | e.a | 0,254 | 4,064 | -
343 | - | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 163 | m | 28,26 | 4606,38 | -
344 | - | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 3 | e.a | 10,2 | 30,6 | -
345 | 3028354.0 | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40x40 | 6,00 | 3 | 40x40 | BW | - | 1 | e.a | 16,00 | 16,00 | -
346 | 3028634.0 | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 6,00 | - | 40 | RF | 150 | 3 | e.a | 10,91 | 32,73 | -
347 | - | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, HO | 6,00 | - | - | RF | 150 | 3 | e.a | 88,00 | 264,00 | -
348 | - | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 6,00 | - | - | RF | 150 | 6 | e.a | 0,302 | 1,812 | -
349 | 3029333.0 | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
350 | 3029333.0 | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 115mm | - | - | - | 16 | e.a | 0,401 | 6,416 | -
351 | 3029333.0 | CS2SA1-6"-SUM-1-6-027 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 125mm | - | - | - | 16 | e.a | 0,42 | 6,72 | -
352 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 2,00 | - | 40 | BE | - | 1 | m | 5,44 | 5,44 | -
353 | 3028425.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 20 | 8,00 | - | 20 | BE | - | 273 | m | 33,32 | 9096,36 | -
354 | 3028560.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 4 | e.a | 9,00 | 36,00 | -
355 | 3028302.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 6 | e.a | 16,57 | 99,42 | -
356 | 3028725.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FT | SOL | SOCKOLET, CS, ASTM A105, MSS SP-97, SW, CLASS 3000 | 8,00 | 0,75 | - | SW | 3000 | 1 | e.a | 0,15 | 0,15 | -
357 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FT | WOL | WELDOLET, CS, ASTM A105, MSS SP-97, BW, SCH 40 | 8,00 | 2 | 20x40 | BW | - | 2 | e.a | 0,79 | 1,58 | -
358 | 3028718.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FL | SW | SOCKETWELD FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,9 | 2,7 | -
359 | 3028631.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 2,00 | - | 40 | RF | 150 | 6 | e.a | 2,55 | 15,3 | -
360 | 3028636.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 20 | 8,00 | - | 20 | RF | 150 | 6 | e.a | 17,3 | 103,8 | -
361 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | VL | BAL | BALL VALVE W/INTEGRAL WELDED 2 NIPPLES, FB, FLOATING BALL, API 608, API 598, A105, CL 800, SW W/2 PE NIPPLES, MNF STD, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, API 607, LO | 0,75 | - | - | PE | 800 | 1 | e.a | 2,4 | 2,4 | -
362 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | VL | BAL | BALL VALVE FL, FB, LP, FLOATING BALL, API 608, A216 GR WCB, CL 150, RF, B16.5, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, SPW SS304/GRAPH, API 607, LO | 2,00 | - | - | RF | 150 | 6 | e.a | 15,00 | 90,00 | -
363 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 8,00 | - | - | RF | 150 | 3 | e.a | 133,00 | 399,00 | -
364 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, HO | 8,00 | - | - | RF | 150 | 6 | e.a | 144,00 | 864,00 | -
365 | 3028740.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | MS | F8 | FIGURE-8 BLANK, CS, ASTM A516 GR 70, ASME B16.48, CLASS 150, RF | 8,00 | - | - | RF | 150 | 6 | e.a | 8,32 | 49,92 | -
366 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,035 | 0,105 | -
367 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 2,00 | - | - | RF | 150 | 12 | e.a | 0,097 | 1,164 | -
368 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 8,00 | - | - | RF | 150 | 18 | e.a | 0,434 | 7,812 | -
369 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 0mm | - | - | - | 4 | e.a | 0,00 | 0,00 | -
370 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 70mm | - | - | - | 4 | e.a | 0,125 | 0,5 | -
371 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 75mm | - | - | - | 4 | e.a | 0,129 | 0,516 | -
372 | 3029340.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 0mm | - | - | - | 16 | e.a | 0,00 | 0,00 | -
373 | 3029340.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 100mm | - | - | - | 16 | e.a | 0,235 | 3,76 | -
374 | 3029340.0 | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,625 | 90mm | - | - | - | 16 | e.a | 0,222 | 3,552 | -
375 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 0mm | - | - | - | 32 | e.a | 0,00 | 0,00 | -
376 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 120mm | - | - | - | 32 | e.a | 0,41 | 13,12 | -
377 | - | CS2SA1-8"-PRO-1-9-020 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 135mm | - | - | - | 32 | e.a | 0,438 | 14,016 | -
378 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 6,00 | - | 40 | BE | - | 1 | m | 28,26 | 28,26 | -
379 | 3028425.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 20 | 8,00 | - | 20 | BE | - | 1 | m | 33,32 | 33,32 | -
380 | 3028560.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 1 | e.a | 9,00 | 9,00 | -
381 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 40 | 6,00 | - | 40 | BW | - | 1 | e.a | 10,2 | 10,2 | -
382 | 3028302.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 4 | e.a | 16,57 | 66,28 | -
383 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | CRE | CONCENTRIC REDUCER, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x40 | 8,00 | 4 | 20x40 | BW | - | 3 | e.a | 6,5 | 19,5 | -
384 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20x40 | 8,00 | 6 | 20x40 | BW | - | 1 | e.a | 28,00 | 28,00 | -
385 | 3028725.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | SOL | SOCKOLET, CS, ASTM A105, MSS SP-97, SW, CLASS 3000 | 8,00 | 0,75 | - | SW | 3000 | 1 | e.a | 0,15 | 0,15 | -
386 | 3028335.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 4 | e.a | 29,00 | 116,00 | -
387 | 3028718.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FL | SW | SOCKETWELD FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,9 | 2,7 | -
388 | 3028633.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 4,00 | - | 40 | RF | 150 | 9 | e.a | 7,11 | 63,99 | -
389 | 3028634.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 6,00 | - | 40 | RF | 150 | 9 | e.a | 10,91 | 98,19 | -
390 | 3028636.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 20 | 8,00 | - | 20 | RF | 150 | 27 | e.a | 17,3 | 467,1 | -
391 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | VL | BAL | BALL VALVE W/INTEGRAL WELDED 2 NIPPLES, FB, FLOATING BALL, API 608, API 598, A105, CL 800, SW W/2 PE NIPPLES, MNF STD, SS316 BALL, SS316 STEM, 2 OR 3 PCS SPLIT BODY SIDE ENTRY, API 607, LO | 0,75 | - | - | PE | 800 | 1 | e.a | 2,4 | 2,4 | -
392 | 3028739.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | MS | F8 | FIGURE-8 BLANK, CS, ASTM A516 GR 70, ASME B16.48, CLASS 150, RF | 6,00 | - | - | RF | 150 | 3 | e.a | 5,39 | 16,17 | -
393 | 3028740.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | MS | F8 | FIGURE-8 BLANK, CS, ASTM A516 GR 70, ASME B16.48, CLASS 150, RF | 8,00 | - | - | RF | 150 | 9 | e.a | 8,32 | 74,88 | -
394 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 0,75 | - | - | RF | 150 | 3 | e.a | 0,035 | 0,105 | -
395 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 6,00 | - | - | RF | 150 | 6 | e.a | 0,302 | 1,812 | -
396 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 8,00 | - | - | RF | 150 | 27 | e.a | 0,434 | 11,718 | -
397 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 0mm | - | - | - | 4 | e.a | 0,00 | 0,00 | -
398 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 70mm | - | - | - | 4 | e.a | 0,125 | 0,5 | -
399 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,5 | 75mm | - | - | - | 4 | e.a | 0,129 | 0,516 | -
400 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 0mm | - | - | - | 48 | e.a | 0,00 | 0,00 | -
401 | 3029333.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
402 | 3029333.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 115mm | - | - | - | 8 | e.a | 0,401 | 3,208 | -
403 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 120mm | - | - | - | 48 | e.a | 0,41 | 19,68 | -
404 | 3029333.0 | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 125mm | - | - | - | 8 | e.a | 0,42 | 3,36 | -
405 | - | CS2SA1-8"-PRO-1-9-022 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 0,75 | 135mm | - | - | - | 48 | e.a | 0,438 | 21,024 | -
406 | - | TRIM-TK-0707 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 24,00 | - | - | RF | 150 | 3 | e.a | 2,216 | 6,648 | -
407 | - | TRIM-TK-0707 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,25 | 190mm | - | - | - | 20 | e.a | 1,721 | 34,42 | -
408 | - | TRIM-TK-0707 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 0mm | - | - | - | 20 | e.a | 0,00 | 0,00 | -
409 | - | TRIM-TK-0707 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,375 | 220mm | - | - | - | 20 | e.a | 2,36 | 47,2 | -
410 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 8,00 | - | 20 | BE | - | 1 | m | 33,32 | 33,32 | -
411 | 3028560.0 | TUBERIA-PAQUETE-BA-05 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 1 | e.a | 9,00 | 9,00 | -
412 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 3 | e.a | 17,3 | 51,9 | -
413 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 12,00 | - | 20 | FF | 150 | 1 | e.a | 37,42 | 37,42 | -
414 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
415 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
416 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
417 | - | TUBERIA-PAQUETE-BA-05 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
418 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 14,00 | - | 30 | BE | - | 4 | m | 81,33 | 325,32 | -
419 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 16,00 | - | 40 | BE | - | 2 | m | 123,31 | 246,62 | -
420 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 2 | e.a | 68,00 | 136,00 | -
421 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30x20 | 14,00 | 8 | 30x20 | BW | - | 1 | e.a | 26,8 | 26,8 | -
422 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 1 | e.a | 93,00 | 93,00 | -
423 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 14,00 | - | 30 | RF | 150 | 24 | e.a | 50,49 | 1211,76 | -
424 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 16,00 | - | 40 | RF | 150 | 6 | e.a | 65,43 | 392,58 | -
425 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 14,00 | - | - | RF | 150 | 3 | e.a | 451,00 | 1353,00 | -
426 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 14,00 | - | - | RF | 150 | 6 | e.a | 406,00 | 2436,00 | -
427 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 16,00 | - | - | RF | 150 | 3 | e.a | 524,00 | 1572,00 | -
428 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 14,00 | - | - | RF | 150 | 18 | e.a | 1,102 | 19,836 | -
429 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 16,00 | - | - | RF | 150 | 6 | e.a | 1,432 | 8,592 | -
430 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 0mm | - | - | - | 104 | e.a | 0,00 | 0,00 | -
431 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 145mm | - | - | - | 72 | e.a | 0,873 | 62,856 | -
432 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 150mm | - | - | - | 32 | e.a | 0,89 | 28,48 | -
433 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 170mm | - | - | - | 72 | e.a | 0,957 | 68,904 | -
434 | - | TUBERIA-PAQUETE-BA-05 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 180mm | - | - | - | 32 | e.a | 0,991 | 31,712 | -
435 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 8,00 | - | 20 | BE | - | 1 | m | 33,32 | 33,32 | -
436 | 3028560.0 | TUBERIA-PAQUETE-BA-06 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 1 | e.a | 9,00 | 9,00 | -
437 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 3 | e.a | 17,3 | 51,9 | -
438 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 12,00 | - | 20 | FF | 150 | 1 | e.a | 37,42 | 37,42 | -
439 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
440 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
441 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
442 | - | TUBERIA-PAQUETE-BA-06 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
443 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 14,00 | - | 30 | BE | - | 4 | m | 81,33 | 325,32 | -
444 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 16,00 | - | 40 | BE | - | 2 | m | 123,31 | 246,62 | -
445 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 2 | e.a | 68,00 | 136,00 | -
446 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30x20 | 14,00 | 8 | 30x20 | BW | - | 1 | e.a | 26,8 | 26,8 | -
447 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 1 | e.a | 93,00 | 93,00 | -
448 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 14,00 | - | 30 | RF | 150 | 24 | e.a | 50,49 | 1211,76 | -
449 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 16,00 | - | 40 | RF | 150 | 6 | e.a | 65,43 | 392,58 | -
450 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 14,00 | - | - | RF | 150 | 3 | e.a | 451,00 | 1353,00 | -
451 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 14,00 | - | - | RF | 150 | 6 | e.a | 406,00 | 2436,00 | -
452 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 16,00 | - | - | RF | 150 | 3 | e.a | 524,00 | 1572,00 | -
453 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 14,00 | - | - | RF | 150 | 18 | e.a | 1,102 | 19,836 | -
454 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 16,00 | - | - | RF | 150 | 6 | e.a | 1,432 | 8,592 | -
455 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 0mm | - | - | - | 104 | e.a | 0,00 | 0,00 | -
456 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 145mm | - | - | - | 72 | e.a | 0,873 | 62,856 | -
457 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 150mm | - | - | - | 32 | e.a | 0,89 | 28,48 | -
458 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 170mm | - | - | - | 72 | e.a | 0,957 | 68,904 | -
459 | - | TUBERIA-PAQUETE-BA-06 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 180mm | - | - | - | 32 | e.a | 0,991 | 31,712 | -
460 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | PP | BE | PIPE, SMLS, CS, ASTM A53 GR B, ASME B36.10, BE, SCH 20 | 8,00 | - | 20 | BE | - | 1 | m | 33,32 | 33,32 | -
461 | 3028560.0 | TUBERIA-PAQUETE-BA-07 | CS1SC2 | FT | 45L | ELBOW 45 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 20 | 8,00 | - | 20 | BW | - | 1 | e.a | 9,00 | 9,00 | -
462 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 8,00 | - | 20 | FF | 150 | 3 | e.a | 17,3 | 51,9 | -
463 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, FF, SCH 20 | 12,00 | - | 20 | FF | 150 | 1 | e.a | 37,42 | 37,42 | -
464 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 8,00 | - | - | FF | 150 | 1 | e.a | 0,09 | 0,09 | -
465 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | GS | GAS | NONMETALLIC FLAT GASKET, ARAMID FIBER REINFORCED NBR, ASME B16.21, THK 1/8", CLASS 150, FF | 12,00 | - | - | FF | 150 | 1 | e.a | 0,19 | 0,19 | -
466 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 0mm | - | - | - | 8 | e.a | 0,00 | 0,00 | -
467 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 120mm | - | - | - | 8 | e.a | 0,41 | 3,28 | -
468 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,75 | 135mm | - | - | - | 8 | e.a | 0,438 | 3,504 | -
469 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,875 | 0mm | - | - | - | 12 | e.a | 0,00 | 0,00 | -
470 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,875 | 135mm | - | - | - | 12 | e.a | 0,617 | 7,404 | -
471 | - | TUBERIA-PAQUETE-BA-07 | CS1SC2 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B1.1/B18.2.2 | 0,875 | 150mm | - | - | - | 12 | e.a | 0,656 | 7,872 | -
472 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 30 | 14,00 | - | 30 | BE | - | 4 | m | 81,33 | 325,32 | -
473 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | PP | BE | PIPE, SMLS, CS, ASTM A106 GR B, ASME B36.10, BE, SCH 40 | 16,00 | - | 40 | BE | - | 2 | m | 123,31 | 246,62 | -
474 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | FT | 90L | ELBOW 90 DEG LR, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 2 | e.a | 68,00 | 136,00 | -
475 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | FT | RTE | REDUCING TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30x20 | 14,00 | 8 | 30x20 | BW | - | 1 | e.a | 26,8 | 26,8 | -
476 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | FT | TEE | STRAIGHT TEE, SMLS, CS, ASTM A234 GR WPB, ASME B16.9, BW, SCH 30 | 14,00 | - | 30 | BW | - | 1 | e.a | 93,00 | 93,00 | -
477 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 30 | 14,00 | - | 30 | RF | 150 | 24 | e.a | 50,49 | 1211,76 | -
478 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | FL | WNK | WELD NECK FLANGE, CS, ASTM A105, ASME B16.5, CLASS 150, RF, SCH 40 | 16,00 | - | 40 | RF | 150 | 6 | e.a | 65,43 | 392,58 | -
479 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | VL | CHS | SWING CHECK VALVE FL, API 594, API 598, A216 GR WCB, CL 150, INST HORIZ/VERT, RF, B16.5, BOLTED COVER, SPW SS304/GRAPH, RENEWABLE SEATS, TRIM #8 | 14,00 | - | - | RF | 150 | 3 | e.a | 451,00 | 1353,00 | -
480 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 14,00 | - | - | RF | 150 | 6 | e.a | 406,00 | 2436,00 | -
481 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | VL | GAT | GATE VALVE FL, API 600, API 598, A216 GR WCB, CL 150, RF, B16.5, BB, SPW SS304/GRAPH, PKG GRAPH, TRIM #8, RENEWABLE SEATS, FLEXIBLE WEDGE, STEM OS&Y/RSNRO, GO | 16,00 | - | - | RF | 150 | 3 | e.a | 524,00 | 1572,00 | -
482 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 14,00 | - | - | RF | 150 | 15 | e.a | 1,102 | 16,53 | -
483 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | GS | GAS | SPIRAL WOUND GASKET, SS, AISI 304/GRAPHITE, ASME B16.20, THK 1/8", CLASS 150, RF | 16,00 | - | - | RF | 150 | 6 | e.a | 1,432 | 8,592 | -
484 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 0mm | - | - | - | 92 | e.a | 0,00 | 0,00 | -
485 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 145mm | - | - | - | 60 | e.a | 0,873 | 52,38 | -
486 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 150mm | - | - | - | 32 | e.a | 0,89 | 28,48 | -
487 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 170mm | - | - | - | 60 | e.a | 0,957 | 57,42 | -
488 | - | TUBERIA-PAQUETE-BA-07 | CS2SA1 | BL | BOLT | STUD BOLTS W/2 HVY HEX NUTS, CS, ASTM A193 GR B7/A194 GR 2H, ASME B18.2.1/B18.2.2 | 1,00 | 180mm | - | - | - | 32 | e.a | 0,991 | 31,712 | -