## BAV24G0I1C
BALL VALVE DATA SHEET
TAG. No. |  | BAV24G0I1C
SIZE : |  | 1 |  | in
PIPING CLASS : |  | CS2SA1 | [11 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | HCN & HCR
M E C H A N I C A L
VALVE TYPE : |  | BALL VALVE, FLOATING BALL | [15 empty] | RATING / CLASS: | 800
END CONNECTIONS: |  | FLANGED | [7 empty] | FACING: | [6 empty] | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [15 empty] | OTHER |  | PE
ENDS SIZE & PRESSURE CLASS PER: | [7 empty] | ASME B16.5 | [6 empty] | ASME B16.11 |  |  |  |  | OTHER |  | MNF STD
BORE: |  | FULL | X | [5 empty] | REDUCED | [6 empty] | ACCORDING TO:
LENGHT: | [6 empty] | SHORT PATTERN | [5 empty] | REG./LONG PATTERN
TYPE OPERATOR : |  | LEVER OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  |  |  | API 6D | [5 empty] | API 608 | X |  |  | API 602 |  |  |  |  | OTHER
APPLICABLE STANDARDS/SPECIFICATIONS : |  |  |  |  | FIRE SAFE AS PER API 607
DESIGN PRESSURE : |  | 285 | [5 empty] | PSIG @100°F | [7 empty] | DESIGN TEMP: |  | 32 |  | F. MIN |  | 100 | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [8 empty] | PSIG |  |  |  |  | TEST PRESSURE: |  |  |  | API 598
CONTAMINANTS : |  | CO2: | [8 empty] | CHLORIDE: | [6 empty] | H2S:
|  | METHANOL : | [11 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM A105 | [13 empty] | PACKING: |  |  | BY MNF
BONNET GASKET: |  | BOLTED CONNECTION: A193 Gr.B7/A194 Gr.2H
SEALS: |  | STEM: GRAPHITE
BALL: |  | AISI 316
STEM : |  | AISI 316
SEAT: |  | RINGS: RPTFE
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | 2 OR 3 PIECES SPLIT BODY SIDE ENTRY, WITH 2 INTEGRAL WELDED PE NIPPLES
N O T E S
1. | Piping Class Doc. No.MTU-ES-01 V1

## BAV24G0I1C (1)
BALL VALVE DATA SHEET
TAG. No. |  | BAV24G0I1C
SIZE : |  | 3/4, 1 |  | in
PIPING CLASS : |  | CS3SA1 | [11 empty] | PLANT LOCATION:
SERVICE (Note 1): |  | HCN & HCR
M E C H A N I C A L
VALVE TYPE : |  | BALL VALVE, FLOATING BALL | [15 empty] | RATING / CLASS: | 800
END CONNECTIONS: |  | FLANGED | [7 empty] | FACING: | [6 empty] | SOCKETWELD |  |  |  | SCREWED
|  | BUTTWELD | [15 empty] | OTHER |  | PE
ENDS SIZE & PRESSURE CLASS PER: | [7 empty] | ASME B16.5 | [6 empty] | ASME B16.11 |  |  |  |  | OTHER |  | MNF STD
BORE: |  | FULL | X | [5 empty] | REDUCED | [6 empty] | ACCORDING TO:
LENGHT: | [6 empty] | SHORT PATTERN | [5 empty] | REG./LONG PATTERN
TYPE OPERATOR : |  | LEVER OPERATOR
D E S I G N
APPLICABLE PIPING
DESIGN CODE: |  | API 600 |  |  |  | API 6D | [5 empty] | API 608 | X |  |  | API 602 |  |  |  |  | OTHER
APPLICABLE STANDARDS/SPECIFICATIONS : |  |  |  |  | FIRE SAFE AS PER API 607
DESIGN PRESSURE : |  | 740 | [5 empty] | PSIG @100°F | [7 empty] | DESIGN TEMP: |  | 32 |  | F. MIN |  | 100 | F. MAX
DESIGN DIFFERENTIAL PRESSURE : | [8 empty] | PSIG |  |  |  |  | TEST PRESSURE: |  |  |  | API 598
CONTAMINANTS : |  | CO2: | [8 empty] | CHLORIDE: | [6 empty] | H2S:
|  | METHANOL : | [11 empty] | OTHERS
M A T E R I A L S
BODY/BONNET: |  | ASTM A105 | [13 empty] | PACKING: |  |  | BY MNF
BONNET GASKET: |  | BOLTED CONNECTION: A193 Gr.B7/A194 Gr.2H
SEALS: |  | STEM: GRAPHITE
BALL: |  | AISI 316
STEM : |  | AISI 316
SEAT: |  | RINGS: RPTFE
COATING: |  | AS PER MTU-ES-12 "ESPECIFICACIÓN TÉCNICA COMPRA VÁLVULAS CORTE Y RETENCIÓN ESTACIONES" AND MTU-ED-04 API TRIM No 8, SOLID WEDGE, BOLTED BONNET A193 Gr. B7/A194 Gr.2H, FLEXIBLE WEDGE
OTHER: |  | 2 OR 3 PIECES SPLIT BODY SIDE ENTRY, WITH 2 INTEGRAL WELDED PE NIPPLES
N O T E S
1. | Piping Class Doc. No.MTU-ES-01 V1